## micom
Code | Description | Value
00.01 | Language | English
00.02 | Password | ****
00.04 | Description | 52-MP-20
00.05 | Plant Reference | 204-MF-02_rev.0
00.06 | Model Number | P241311B2M0600J
00.08 | Serial Number | 690927U
00.09 | Frequency | 60 Hz
00.0A | Comms Level | 2
00.0B | Relay Address | 1
00.0C | Plant Status | 0000000000000010
00.0D | Control Status | 0000000000000000
00.0E | Active Group | 1
00.10 | CB Trip/Close | No Operation
00.11 | Software Ref. 1 | P241 60C
00.20 | Opto I/P Status | 00000001
00.21 | Relay O/P Status | 0000000
00.22 | Alarm Status 1 | 10000000000000000000001000000100
00.50 | Alarm Status 1 | 10000000000000000000001000000100
00.51 | Alarm Status 2 | 00000000000000000000000000000000
00.52 | Alarm Status 3 | 00000000000000000000000000000000
00.D0 | Access Level | 2
00.D1 | Password Control | 2
00.D2 | Password Level 1 | ****
00.D3 | Password Level 2 | ****
07.01 | CB Control by | Disabled
08.01 | Date/Time | 2019-08-15 11:57:01.636
08.06 | Battery Status | Healthy
08.07 | Battery Alarm | Enabled
08.20 | LocalTime Enable | Fixed
08.21 | LocalTime Offset | 0 min
08.22 | DST Enable | Enabled
08.23 | DST Offset | 60.00 min
08.24 | DST Start | Last
08.25 | DST Start Day | Sunday
08.26 | DST Start Month | March
08.27 | DST Start Mins | 60.00 min
08.28 | DST End | Last
08.29 | DST End Day | Sunday
08.2A | DST End Month | October
08.2B | DST End Mins | 60.00 min
09.01 | Restore Defaults | No Operation
09.02 | Setting Group | Select via Menu
09.03 | Active Settings | Group 1
09.04 | Save Changes | No Operation
09.05 | Copy From | Group 1
09.06 | Copy To | No Operation
09.07 | Setting Group 1 | Enabled
09.08 | Setting Group 2 | Disabled
09.0B | Thermal Overload | Enabled
09.0C | Short Circuit | Enabled
09.0D | Sensitive E/F | Enabled
09.0E | Neg Seq O/C | Enabled
09.0F | 3Ph Volt.Check | Disabled
09.10 | Derived E/F | Disabled
09.11 | Neg Seq O/V | Disabled
09.14 | Stall Detection | Enabled
09.16 | Residual O/V NVD | Disabled
09.17 | Limit nb Starts | Enabled
09.18 | Loss of Load | Disabled
09.19 | Out of Step | Disabled
09.1A | Reverse power | Disabled
09.1B | Antibackspin | Disabled
09.1C | Field Failure | Disabled
09.1D | Volt Protection | Enabled
09.1E | Under Frequency | Disabled
09.1F | RTD Inputs | Enabled
09.20 | CB Fail | Enabled
09.21 | Supervision | Disabled
09.24 | System Config | Invisible
09.25 | Input Labels | Visible
09.26 | Output Labels | Visible
09.27 | RTD Labels | Visible
09.28 | CT & VT Ratios | Visible
09.29 | Record Control | Invisible
09.2A | Disturb Recorder | Visible
09.2B | Measure't Setup | Visible
09.2C | Comms Settings | Visible
09.2D | Commission Tests | Visible
09.2E | Setting Values | Primary
09.2F | Control Inputs | Visible
09.35 | Ctrl I/P Config | Invisible
09.36 | Ctrl I/P Labels | Invisible
09.39 | Direct Access | Enabled
09.FB | RP1 Read Only | Disabled
0A.01 | Main VT Primary | 13.80 kV
0A.02 | Main VT Sec'y | 120.0 V
0A.07 | Phase CT Primary | 150.0 A
0A.08 | Phase CT Sec'y | 5.000 A
0A.0B | SEF CT Primary | 50.00 A
0A.0C | SEF CT Secondary | 5.000 A
0A.11 | VT Connect. Mode | 2 VT + Residual
0A.12 | NVD VT Primary | 110.0 V
0A.13 | NVD VT Secondary | 110.0 V
0C.01 | Duration | 10.00 s
0C.02 | TriggerPosition | 30.00 %
0C.03 | TriggerMode | Extended
0C.04 | AnalogChannel1 | IN
0C.05 | AnalogChannel2 | IN
0C.06 | AnalogChannel3 | IN
0C.07 | AnalogChannel4 | IA
0C.08 | AnalogChannel5 | IB
0C.09 | AnalogChannel6 | IC
0C.0A | AnalogChannel7 | IN
0C.0B | AnalogChannel8 | IN
0C.0C | DigitalInput1 | Strt in Progress
0C.0D | Input1Trigger | Trigger L/H
0C.0E | DigitalInput2 | Trip V<2
0C.0F | Input2Trigger | Trigger L/H
0C.10 | DigitalInput3 | Relay Label 03
0C.11 | Input3Trigger | Trigger L/H
0C.12 | DigitalInput4 | Relay Label 04
0C.13 | Input4Trigger | No trigger
0C.14 | DigitalInput5 | Relay Label 05
0C.15 | Input5Trigger | No trigger
0C.16 | DigitalInput6 | Relay Label 06
0C.17 | Input6Trigger | No trigger
0C.18 | DigitalInput7 | Relay Label 07
0C.19 | Input7Trigger | No trigger
0C.1A | DigitalInput8 | Unused
0C.1C | DigitalInput9 | Unused
0C.1E | DigitalInput10 | Unused
0C.20 | DigitalInput11 | Unused
0C.22 | DigitalInput12 | Unused
0C.24 | DigitalInput13 | Unused
0C.26 | DigitalInput14 | Unused
0C.28 | DigitalInput15 | Unused
0C.2A | DigitalInput16 | Unused
0C.2C | DigitalInput17 | Unused
0C.2E | DigitalInput18 | Unused
0C.30 | DigitalInput19 | Unused
0C.32 | DigitalInput20 | Unused
0C.34 | DigitalInput21 | Unused
0C.36 | DigitalInput22 | Unused
0C.38 | DigitalInput23 | Unused
0C.3A | DigitalInput24 | Unused
0C.3C | DigitalInput25 | Unused
0C.3E | DigitalInput26 | Unused
0C.40 | DigitalInput27 | Unused
0C.42 | DigitalInput28 | Unused
0C.44 | DigitalInput29 | Unused
0C.46 | DigitalInput30 | Unused
0C.48 | DigitalInput31 | Unused
0C.4A | DigitalInput32 | Unused
0D.01 | Default Display | 3Ph + N Current
0D.02 | Local Values | Primary
0D.03 | Remote Values | Primary
0D.04 | Measurement Ref | VA
0D.06 | Demand Interval | 30.00 min
0D.07 | Alarm Fix Dem. | Invisible
0D.0A | Alarm Energies | Invisible
0D.0F | Motor Hour Run>1 | Disabled
0D.11 | Motor Hour Run>2 | Disabled
0F.01 | Opto I/P Status | 00000001
0F.02 | Relay O/P Status | 0000000
0F.03 | Test Port Status | 00000000
0F.04 | LED Status | 00000000
0F.05 | Monitor Bit 1 | Relay Label 01
0F.06 | Monitor Bit 2 | Relay Label 02
0F.07 | Monitor Bit 3 | Relay Label 03
0F.08 | Monitor Bit 4 | Relay Label 04
0F.09 | Monitor Bit 5 | Relay Label 05
0F.0A | Monitor Bit 6 | Relay Label 06
0F.0B | Monitor Bit 7 | Relay Label 07
0F.0C | Monitor Bit 8 | Opto Label 01
0F.0D | Test Mode | Disable
0F.0E | Test Pattern | 0000000
0F.0F | Contact Test | No operation
0F.10 | Test LEDs | No operation
0F.30 | DDB 543 - 512 | 00000000000000000000000000000000
0F.31 | DDB 575 - 544 | 00000000000000000000000000000000
0F.32 | DDB 607 - 576 | 00000000000000000000000000000000
0F.33 | DDB 639 - 608 | 00000000000000000000000000000000
0F.34 | DDB 671 - 640 | 00000000000000000000000000000000
0F.35 | DDB 703 - 672 | 00000000000000000000000000000000
0F.36 | DDB 735 - 704 | 00000000000000000000000000000000
0F.37 | DDB 767 - 736 | 00000000000000000000000000000000
0F.38 | DDB 799 - 768 | 00000000000000000000000000000000
0F.39 | DDB 831 - 800 | 00000000000000000000000000000000
0F.3A | DDB 863 - 832 | 00000000000000000000000000000000
0F.3B | DDB 895 - 864 | 00000000000000000000000000000000
0F.3C | DDB 927 - 896 | 00100000000000000000000000000000
0F.3D | DDB 959 - 928 | 00000000000000000000000000000000
0F.3E | DDB 991 - 960 | 00000000000000000000000000000000
0F.3F | DDB 1023 - 992 | 00000000000000000000000000000000
0F.40 | DDB 1055 - 1024 | 00000000000000000000000000000000
0F.41 | DDB 1087 - 1056 | 00000000000000000000000000000000
0F.42 | DDB 1119 - 1088 | 00000000000000000000000000000000
0F.43 | DDB 1151 - 1120 | 00000000000000000000000000000000
0F.44 | DDB 1183 - 1152 | 00000000000000000000000000000000
0F.45 | DDB 1215 - 1184 | 00000000000000000000000000000000
0F.46 | DDB 1247 - 1216 | 00000000000000000000000000000000
0F.47 | DDB 1279 - 1248 | 00000000000000000000000000000000
0F.48 | DDB 1311 - 1280 | 00000000000000000000000000000000
0F.49 | DDB 1343 - 1312 | 00000000000000000000000000000000
0F.4A | DDB 1375 - 1344 | 00000000000000000000000000000000
0F.4B | DDB 1407 - 1376 | 00000000000000000000000000000000
0F.4C | DDB 1439 - 1408 | 00000000000000000000000000000000
0F.4D | DDB 1471 - 1440 | 00000000000000000000000000000000
0F.4E | DDB 1503 - 1472 | 00000000000000000000000000000000
0F.4F | DDB 1535 - 1504 | 00000000000000000000000000000000
0F.50 | DDB 1567 - 1536 | 00000000000000000000000000000000
0F.51 | DDB 1599 - 1568 | 00000000000000000000000000000000
0F.52 | DDB 1631 - 1600 | 00000000000000000000000000000000
0F.53 | DDB 1663 - 1632 | 00000000000000000000000000000000
0F.54 | DDB 1695 - 1664 | 00000000000000000000000000000000
0F.55 | DDB 1727 - 1696 | 00000000000000000000000000000000
0F.56 | DDB 1759 - 1728 | 00000000000000000000000000000000
0F.57 | DDB 1791 - 1760 | 00000000000000000000000000000000
0F.58 | DDB 1823 - 1792 | 00000000000000000000000000000000
0F.59 | DDB 1855 - 1824 | 00000000000000000000000000000000
0F.5A | DDB 1887 - 1856 | 00000000000000000000000000000000
0F.5B | DDB 1919 - 1888 | 00000000000000000000000000000000
0F.5C | DDB 1951 - 1920 | 00000000000000000000000000000000
0F.5D | DDB 1983 - 1952 | 00000000000000000000000000000000
0F.5E | DDB 2015 - 1984 | 00000000000000000000000000000000
0F.5F | DDB 2047 - 2016 | 00000000000000000000000000000000
10.01 | Broken I^ | 2.000
10.02 | I^ Maintenance | Disabled
10.06 | No CB Ops Maint | Disabled
10.0A | CB Time Maint | Disabled
11.01 | Global Nominal V | 110/125V
11.50 | Opto Filter Cntl | 11111111
11.80 | Characteristic | Standard 60%-80%
30.01 | Ith Current Set | 88.50 A
30.02 | K Coefficient | 3
30.03 | Thermal Const T1 | 18.00 min
30.04 | Thermal Const T2 | 18.00 min
30.05 | Cooling Const Tr | 198.0 min
30.06 | Thermal Trip | Enabled
30.07 | Thermal Alarm | Enabled
30.08 | Alarm Threshold | 93.00 %
30.09 | Thermal Lockout | Enabled
30.0A | Lockout Thresh. | 85.00 %
30.0B | Inh.Trip dur St. | Disabled
30.0C | Thermal Overload | Thermal Model
31.01 | I>1 Function | DT
31.02 | I>1 Current Set | 690.0 A
31.03 | I>1 Time Delay | 40.00 ms
31.11 | I>2 Function | Disabled
31.21 | I>3 Function | Disabled
31.31 | I>4 Function | Disabled
32.01 | ISEF>1 Function | DT
32.02 | ISEF>1 Direction | Non Directional
32.03 | ISEF>1 Current | 15.00 A
32.04 | ISEF>1 T. Delay | 40.00 ms
32.09 | ISEF>2 Function | Disabled
32.10 | GROUP 1 WATTMETRIC SEF
32.11 | P0> Function | Disabled
33.01 | I2>1 Status | DT
33.02 | I2>1 Current Set | 18.75 A
33.03 | I2>1 Time Delay | 3.000 s
33.04 | I2>2 Status | Disabled
39.01 | Prolonged Start | Enabled
39.02 | Start Criteria | 52a
39.03 | Starting Current | 225.0 A
39.04 | Prol. Start Time | 5.000 s
39.05 | Stall Rotor-strt | Disabled
39.06 | Stall Detection | Enabled
39.07 | Stall Setting | 225.0 A
39.08 | Stall Time | 3.000 s
39.09 | Reacceleration | Enabled
39.0A | Reac. Low V Set | 11.50 kV
39.0B | LV Ride Thru | Disabled
3C.01 | Hot Start Status | Enabled
3C.02 | Hot Start Nb. | 1
3C.03 | Cold Start Stat. | Enabled
3C.04 | Cold Start Nb. | 3
3C.05 | Supervising Time | 60.00 min
3C.06 | T.Betw.St.Status | Disabled
3C.08 | Inhib.Start Time | 30.00 min
42.01 | GROUP 1 UNDER VOLTAGE
42.02 | V< Measur't Mode | Phase-Phase
42.03 | V< Operate Mode | Three Phase
42.04 | V<1 Function | DT
42.05 | V<1 Voltage Set | 3450 V
42.06 | V<1 Time Delay | 500.0 ms
42.09 | V<2 Status | DT
42.0A | V<2 Voltage Set | 12.42 kV
42.0B | V<2 Time Delay | 250.0 ms
42.0C | Inhib.During St. | Disabled
42.0D | GROUP 1 OVERVOLTAGE
42.0E | V> Measur't Mode | Phase-Phase
42.0F | V> Operate Mode | Any Phase
42.10 | V>1 Status | Disabled
42.14 | V>2 Status | Disabled
44.01 | Select RTD | 0000111111
44.03 | RTD 1 Alarm Set | 130.0 Cel
44.04 | RTD 1 Alarm Dly | 5.000 s
44.05 | RTD 1 Trip Set | 155.0 Cel
44.06 | RTD 1 Trip Dly | 3.000 s
44.08 | RTD 2 Alarm Set | 130.0 Cel
44.09 | RTD 2 Alarm Dly | 5.000 s
44.0A | RTD 2 Trip Set | 155.0 Cel
44.0B | RTD 2 Trip Dly | 3.000 s
44.0D | RTD 3 Alarm Set | 130.0 Cel
44.0E | RTD 3 Alarm Dly | 5.000 s
44.0F | RTD 3 Trip Set | 155.0 Cel
44.10 | RTD 3 Trip Dly | 3.000 s
44.12 | RTD 4 Alarm Set | 130.0 Cel
44.13 | RTD 4 Alarm Dly | 5.000 s
44.14 | RTD 4 Trip Set | 155.0 Cel
44.15 | RTD 4 Trip Dly | 3.000 s
44.17 | RTD 5 Alarm Set | 130.0 Cel
44.18 | RTD 5 Alarm Dly | 5.000 s
44.19 | RTD 5 Trip Set | 155.0 Cel
44.1A | RTD 5 Trip Dly | 3.000 s
44.1C | RTD 6 Alarm Set | 130.0 Cel
44.1D | RTD 6 Alarm Dly | 5.000 s
44.1E | RTD 6 Trip Set | 155.0 Cel
44.1F | RTD 6 Trip Dly | 3.000 s
44.34 | Ext.Temp.Influen | Disabled
44.50 | RTD Type | PT100
44.51 | RTD Unit | Celcius
45.01 | GROUP 1 CB FAIL
45.02 | CB Fail 1 Status | Disabled
45.08 | GROUP 1 UNDER CURRENT
45.09 | I< Current Set | 9.000 A
4A.01 | Opto Input 1 | 52 Fechado
4A.02 | Opto Input 2 | 52 Aberto
4A.03 | Opto Input 3 | OPTO 3
4A.04 | Opto Input 4 | OPTO 4
4A.05 | Opto Input 5 | OPTO 5
4A.06 | Opto Input 6 | OPTO 6
4A.07 | Opto Input 7 | OPTO 7
4A.08 | Opto Input 8 | OPTO 8
4B.01 | Relay 1 | 50 BF
4B.02 | Relay 2 | Desliga sub tens
4B.03 | Relay 3 | Trip rele 86
4B.04 | Relay 4 | Sel Log 00-MF-24
4B.05 | Relay 5 | Sel Log MF-1C
4B.06 | Relay 6 | RELAY 6
4B.07 | Relay 7 | Bloq fech 52-02
4C.01 | RTD 1 | RTD 1 - FASE R
4C.02 | RTD 2 | RTD 2 - FASE S
4C.03 | RTD 3 | RTD 3 - FASE T
4C.04 | RTD 4 | RTD 4 - FASE R
4C.05 | RTD 5 | RTD 5 - FASE S
4C.06 | RTD 6 | RTD 6 - FASE T